OPERATION & MAINTENANCE

| OPERATOR DAILY ROUTINE JOBS & CHECKLIST |  |
| --- | --- |
| JOB DESCRIPTION | REMARKS |
| HIGH PRESSURE PUMP(S) AND OTHER CENTRIFUGAL PUMPS |  |
| Check the following : 1. Motor current and voltage 2. Noise 3. Vibration 4. Discharge and suction pressure 5. Seal leakage 6. Bearing temperature 7. Lubricant oil level | Daily Once pr. shift |
| CHEMICAL DOSING PUMPS |  |
| Check for : 1. Noise 2. Vibration 3. Leakage from pipe connections | Once pr. shift |
| CHEMICAL DOSING TANKS AND MIXERS |  |
| Check for : 1. Leakage 2. Noise 3. Vibration | Once pr. shift When mixer is operated |
| DEGASSIFIER |  |
| Check for : 1. Noise 2. Vibration 3. Water Flow | Once pr. shift |
|  | (Continue next page) |

| OPERATOR DAILY ROUTINE JOBS & CHECKLIST |  |
| --- | --- |
| JOB DESCRIPTION | REMARKS |
| (Cont'd) |  |
| AIR BLOWER |  |
| Check for : 1. Noise 2. Vibration 3. Blower temperature 4. Lubricant oil level 5. Belt wear | Once pr. shift |
| AIR COMPRESSOR |  |
| Check for : 1. Noise 2. Vibration 3. Lubricant oil level 4. Drain air receiver | Once pr. shift |
| INSPECTION ROUND AT EACH SHIFT |  |
| Check for : |  |
| 1. Leakage pipe points |  |
| 2. Leaking valves |  |
| 3. Loose cable connections |  |
| 4. Fraying, wear or damage to electrical cables and instrument leads |  |

| INSTRUMENT READINGS |  |  |
| --- | --- | --- |
| JOB DESCRIPTION | REMARKS |  |
| FLOWS |  |  |
| RAW WATER INLET | Every 2nd hour |  |
| R.O FEED | Twice pr. shift |  |
| PERMEATE BRINE | (= every 4 hours). Every 2nd hour |  |
|  | during Plant startup |  |
| FILTER PRESSURES |  |  |
| MEDIA FILTER INLET |  |  |
| MEDIA FILTER OUTLET | Once pr. shift, |  |
| PRESSURE DIFF., MEDIA FILTERS |  |  |
| PRESSURE DIFF., CARTR. FILTERS | Twice pr. shift, |  |
|  | (=every 4 hours |  |
| PRESSURES, R.O UNITS |  |  |
| HIGH PRESS. PUMP, DISCHARGE R.O OPERATING PRESSURE INTERSTAGE PRESSURE PERMEATE BRINE R.O DIFFERENTIAL PRESSURE | Twice pr. shift (= every 4 hours Every 2nd hour during Plant startup | Verify if more than one stage |
| OTHER PRESSURE READINGS |  |  |
| RAW WATER PUMPS |  |  |
| FILTER FEED PUMPS |  |  |
| BACKWASH PUMPS | Once pr. day |  |
| FINAL PRODUCT PUMPS |  |  |
| DEGASSIFIED WATER PUMPS |  |  |
| CLEANING PUMPS FLUSHING PUMPS POST-TREATMENT PUMPS AIR BLOWER AIR COMPRESSOR | (Continue next page) |  |

| INSTRUMENT READINGS |  |
| --- | --- |
| JOB DESCRIPTION | REMARKS |
| (Cont’d) |  |
| TEMPERATURE |  |
| FILTERED WATER OUTLET (common R.O feed) | Once pr. shift |
| R.O FEED (for each R.O unit aftercartr. filter) | Once pr. shift., ref. Attachment A5 and every 2nd hour during Plant startup, |
| ORP & pH |  |
| R.O FEED | Twice pr. shift |
|  | (= every 4 hours). |
|  | Every 2nd hour |
|  | during Plant startup |
| CONDUCTIVITY |  |
| R.O FEED | Twice pr. shift |
| PERMEATE | (=every 4 hours). |
|  | Every 2nd hour |
|  | during Plant startup |
| RUNNING HOURS |  |
| RAW WATER PUMPS |  |
| FILTER FEED PUMPS |  |
| BACKWASH PUMPS |  |
| R.O HIGH PRESSURE PUMPS |  |
| FINAL PRODUCT PUMPS |  |
| DEGASSIFIED WATER PUMPS | Weekly |
| CLEANING PUMPS |  |
| FLUSHING PUMPS |  |
| POST-TREATMENT PUMPS |  |
| AIR BLOWERS |  |
| AIR COMPRESSOR |  |
|  | (Continue next page) |

| INSTRUMENT READINGS |  |
| --- | --- |
| JOB DESCRIPTION | REMARKS |
| (Cont'd) |  |
| TANK LEVELS |  |
| RAW WATER |  |
| FINAL PRODUCT | Once to twice |
| BACKWASH | pr. shift |
| REJECT WATER |  |

| LABORATORY & INSTRUMENT TESTS |  |
| --- | --- |
| JOB DESCRIPTION | REMARKS |
| TURBIDITY |  |
| RAW WATER | Once pr. shift |
| SDI |  |
| MEDIA FILTER OUTLET | Once pr. shift |
| R.O FEED (after microfilter) | Once pr. shift. Every 2nd hour |
|  | during Plant startup |
| LSI or S&DSI |  |
| LAST STAGE BRINE FLOW | Monthly |
| TOTAL IRON | Once pr. shift during |
|  | Plant startup |
| MEDIA FILTER OUTLET | (If BIRM Filters are reqd. due to |
|  | high iron in raw water, regular |
|  | regular iron tests are required) |
| TDS |  |
| RAW WATER | Once pr. shift |
| R.O FEED |  |
| PERMEATE of each stage | Once pr. month |
| BRINE |  |
| EACH PRESSURE VESSEL | Once pr. week |
| FINAL PRODUCT WATER | Once pr. shift |
| pH |  |
| FINAL PRODUCT WATER | Once pr. (Continue next page) |

| LABORATORY & INSTRUMENT TESTS |  |
| --- | --- |
| JOB DESCRIPTION | REMARKS |
| FREE RESIDUAL CHLORINE |  |
| RAW WATER | Once pr. shift |
| FINAL PRODUCT | Once pr. shift |
| SULPHATE |  |
| CARTRIDGE FILTER OUTLET | Once pr. shift |
| ALKALINITY |  |
| CARTRIDGE FILTER OUTLET | Once pr. shift |
| CHLORIDE & CONDUCTIVITY |  |
| R.O FEED | Eight (8) times |
| PERMEATE of each stage | pr. month |
| BRINE | ( Twice a week) |
| TEMPERATURE |  |
| RAW WATER | Once pr. shift |
| TOTAL BACTERIAL COUNT (TBC) |  |
| R.O FEED |  |
| PERMEATE of each stage | Once pr. month |
| BRINE |  |
| COMPLETE WATER ANALYSIS |  |
| RAW WATER |  |
| R.O FEED | Quarterly |
| PERMEATE | (every 3 months) |
| BRINE |  |

| R.O PRE-STARTUP CHECK LIST |  |
| --- | --- |
| JOB DESCRIPTION | REMARKS |
| Rotating Equipment |  |
| 1. Before inspection of rotating parts, power supply should be shut off at the Control Panels. Manual isola-tion valves are closed | Before starting up this Plant each unit shall be checked in accordance with the procedures as described |
| 2. Confirm that lubricant oil level is normal and oil is clean. Changing of oil shall be done at regular intervals in accordance with the Lubrication Schedule |  |
| 3. Confirm that the rotating friction element is correctly greased. Makeup or replacement of grease is carried out in accordance with Lubrication Schedule |  |
| 4. Confirm that the rotating equipment is correctly coupled with its drive and securely bolted to the base |  |
| 5. Make sure that coupling alignment is accurate |  |
| 6. Confirm that external cooling/ flushing water is supplied as required |  |
| 7. Confirm by hand that the rotating element is free and check direction of rotation |  |
| 8. Verify that the isolation valves are operational |  |
|  | (Continue next page) |

| R.O PRE-STARTUP CHECK LIST |  |
| --- | --- |
| JOB DESCRIPTION | REMARKS |
| (Cont'd) |  |
| 9. Grease up all points |  |
| 10. All water pumps must be fully primed and air vented |  |
| 11. Action a short test run to ensure that there is no abnormal sound or vibration | NEVER START PUMP UNDER DRY CONDITION |
| 12. For motors coupled to a Gear Unit: start pump again for a few seconds and stop. Repeat this three to four times to ensure lubrication of gear box is complete (for R.O High Pressure Pumps, confirm that water is seen dripping from mechanical seal) |  |
| R.O Units |  |
| 1. Open all manual isolation valves on feed, brine and product (permeate) lines |  |
| Pressure Sand / Carbon Filters |  |
| 1. Open all Filter Inlet/Outlet Valves |  |
| 2. Close other valves (including drain valve) |  |
| 3. Check that manholes are closed |  |
| 4. Check that Pressure Indicators, analysis element sample valves, Flow Control Valve(s) etc., all are installed in correct positions | (Continue next page) |

| R.O PRE-STARTUP CHECK LIST |  |
| --- | --- |
| JOB DESCRIPTION | REMARKS |
| (Cont'd) |  |
| Cartridge Filters |  |
| 1. Open air vent valve until all air is expelled and close valve |  |
| 2. Open isolation valves of filter vessel |  |
| 3. Open drain valve after cartridge filter and check for SDI |  |
| 4. Close drain valve when SDI is as required |  |
| Degassifier |  |
| 1. Open inlet and outlet valves |  |
| 2. Check that power supply to fan motor is corresponding to the voltage and frequency as shown on name plate |  |
| 3. Check that the fan rotates freely in correct direction |  |
| 4. Ensure packing media is installed inside tower |  |
| 5. Check that the float switches are installed in correct position and ensure that the float is moving freely on the chain/rod |  |
| 6. Check that the bearings are filled with the correct grade and quantity of grease |  |
|  | (Continue next page) |

| R.O PRE-STARTUP CHECK LIST |  |
| --- | --- |
| JOB DESCRIPTION | REMARKS |
| (Cont'd) |  |
| Chemical Dosing Tanks |  |
| 1. Check that new chemical solutions for all chemical feed systems have been filled |  |
| 2. Adjust stroke frequency and/or stroke length knobs as required |  |
| 3. Open all manual isolation valves |  |
| 4. For Sulphuric Acid, make sure that siphon valves are piped back to tank |  |
| 5. Check that the tubing and valves are correctly connected |  |
| Water Tanks |  |
| 1. Check that isolation valves are installed in correct position |  |
| 2. Check that the float or level switches are installed in the correct position (if present) |  |
| 3. Close all manholes |  |
| 4. Check that the pressure switches installed on the tank are at required set point (if required) |  |
|  | (Continue next page) |

| R.O PRE-STARTUP CHECK LIST |  |
| --- | --- |
| JOB DESCRIPTION | REMARKS |
| (Cont'd) |  |
| Membrane Cleaning System |  |
| 1. Check Cleaning Pump with same procedure as "Rotating Equip-ment" |  |
| 2. Check "Cleaning Cartridge Filter" with same procedure as "Cartridge Filters" |  |
| 3. Purge all air from the piping line if vent valves are available |  |
| 4. Check that level in Cleaning Tank is enough |  |
| 5. Open the block valves of piping line |  |
| U.V Sterilizer |  |
| 1. Check that the U.V Sterilizer is properly grounded |  |
| 2. Open the inlet valves |  |
| 3. Check power supply to the unit |  |
| 4. Check that the U.V lamps are free and clean from paper warning tags or from any debris |  |
| Pipelines & Valves |  |
| 1. Vent all air from water pipe lines |  |
| 2. Open/close the block valves as required | (Continue next page) |

| R.O PRE-STARTUP CHECK LIST |  |
| --- | --- |
| JOB DESCRIPTION | REMARKS |
| (Cont'd) |  |
| 3. Close air vent and drain valves after flushing |  |
| 4. Drain all water from air pipeline |  |
| 5. Check pipe supports |  |
| 6. Check pipe and fittings |  |
| Electric Equipment & Instruments |  |
| 1. Check that control and power cabling is correct | Following description shows an outline of check items for electrical equipment and instruments. Details are given at individual sections of this O & M Manual |
| 2. Make sure sequence check and interlock check |  |
| 3. Check that power supply is available |  |
| 4. Check that selector switches of electrical eqipment are in correct position |  |
| 5. Check the insulation resistance of transmitter coils |  |
| 6. Confirm that analyzers are ready for operation |  |
| 7. Confirm that all instruments are correctly indicated and calibrated |  |
| 8. Make sure that all ORP equipment are calibrated on site during operation |  |
|  | (Continue next page) |

| R.O PRE-STARTUP CHECK LIST |  |
| --- | --- |
| JOB DESCRIPTION | REMARKS |
| (Cont'd) |  |
| Control Panels : |  |
| 1. Check the voltage and frequency of electric power supply |  |
| 2. Check all panel mounted equip-ment and calibrate |  |
| 3. Lamp test |  |
| 4. Interlock and sequence check |  |

| R.O PLANT STARTUP |  |
| --- | --- |
| JOB DESCRIPTION | REMARKS |
| Preliminary checks |  |
| Before starting make sure that : 1. Raw water is available and it meets the required quality 2. The feed pump systems are opera-tional (Filter Feed Pumps and R.O High Pressure Pumps) | The Plant is assumed to be off line and all selector switches are set to "Off ". If the Plant is in log term storage condition, i.e. filled with sanitizing fluid then it will be necessary to initially flush the product to drain by disconnecting the product discharge piping and connecting a hose |
| 3. The filter(s) have been back-washed and the valves are set to service position |  |
| 4. All necessary valves on the raw water line are open |  |
| 5. 5 micron (5µ) rated cartridges are correctly fitted in the housing for pre-treatment Cartridge Filters |  |
| 6. All Chemical Dosing Tank contains solution |  |
| 7. All Chemical Dosing Pumps are primed |  |
| 8. Strokes and speeds of all Dosing Pumps are correctly set |  |
| Filling of Backwash Tank |  |
| In normal operation, the Backwash Tank is being replenished continuously by R.O product water | When the R.O Units are not operating, there will be no water for backwashing the filters apart from what is stored in the Backwash Tank |
|  | (Continue next page) |

| R.O PLANT STARTUP |  |
| --- | --- |
| JOB DESCRIPTION | REMARKS |
| (Cont'd) |  |
| Filling of filters |  |
| The filters must be filled with water before they are put in service. Each filter is filled by manually operating the backwash system and filter valves as follows : |  |
| 1. Verify that the Backwash Tank is full of water | During plant startup it will be necessary to fill the tank with water |
| 2. Select the filter to be filled. Open Backwash Inlet and Backwash Outlet Valves for that filter | The other filter valves should be closed |
| 3. Open the suction valve for the Backwash Pump to be used for filter filling and keep discharge valve closed |  |
| 4. Start the pump by placing its selector switch in Manual-position. As soon as the pump starts, manually open the Backwash Outlet Valve. Limit the flow to L/s |  |
| 5. When the filter is full, close the discharge valve and switch the Backwash Pump to "Off " |  |
| 6. Repeat above steps for each filter until all filters are filled |  |
|  | (Continue next page) |

| R.O PLANT STARTUP |  |  |  |  |
| --- | --- | --- | --- | --- |
| JOB DESCRIPTION | REMARKS |  |  |  |
| (Cont'd) |  |  |  |  |
| Startup Procedure |  |  |  |  |
| 1. Startup preparation (Plant line up) | When starting the R.O Unit for the first time, the following checks should be per-formed to ensure safety of equipment and personnel and to exclude possible malfunction : a. Insulation test should be done using a megaohm tester when power cables are disconnected from motors, panel deenergized. Insula-tion resistance should not be less than 5 megaohms b. Dry run test should be performed when power circuit breaker for motors are "Off " and control circuit energized. This test consists of a simulation to make sure that the process will be controlled properly |  |  |  |
| 2. Fill media filters (Sand and Carbon Filters) with water |  |  |  |  |
| 3. Prepare chemical solutions |  | Fe (SO4)3, H2SO4, NaOCl, CaCl2, NaOH, HCl, NaCl, etc. |  | Verify |
| 4. Startup of filtration systems (Sand/Carbon Filters) |  |  |  |  |
| 5. Startup of Chemical Dosing Pumps |  |  |  |  |
| 6. Open Cartridge Filters |  |  |  |  |
|  | (Continue next page) |  |  |  |

| R.O PLANT STARTUP |  |
| --- | --- |
| JOB DESCRIPTION | REMARKS |
| (Cont'd) |  |
| 7. Check pH, Temp., SDI, Cl2, Biological matter, F, Ba++, Sr++, Iron... etc. | 6.5 < pH < 7.5 Temp. < 35oC SDI : as per guidelines Cl2 = 0 mg/L If OK: Go to Biological matter : none Step 8. Ba++ = 0 mg/L ion If not: Wait Sr++ = 0 mg/L ion until OK F = 0 mg/L ion Total Iron = < mg/L |
| 8. Start R.O High Pressure Pump |  |
| 9. Start Degassifier Fan |  |
| 10. Start Degassified Water Pumps |  |
| 11. Startup Final Product Pumps/ Potable Water Pumps |  |
| 12. Startup potable water Post-treat-ment Chemical Feed Systems |  |
|  | Note : Before operating any pump manually, check the water level at upstream tank contains enough water for operation |

| R.O PLANT SHUTDOWN |  |
| --- | --- |
| JOB DESCRIPTION | REMARKS |
| 1. Stop R.O High Pressure Pumps 2. Flush R.O Units using feed water 3. Stop Degassifier and Final Product Pumps | Note : Only stop R.O Unit by switching the main power switch to "Off " in event of an emergency ; never else  |
| 4. Stop Raw Water Pumps 5. Stop all Chemical Dosing Pumps | Note : When stopping for more than two (2) days, membranes must be prepared for "long term storage" by filling with sterilizing solution, see step 8 |
| 6. Backwash the filter(s), then stop Air Blowers |  |
| 7. Stop filtration system by shutting down Filter Feed Pumps. Close Sand/Carbon Filters and Cartridge Filters | If shutdown period is greater than two (2) days : Go to step 8. If not : Go to step 9 |
| 8. Fill R.O membranes with 1.0 wt % Formaldehyde | To prevent growth within membranes |
| 9. Daily operation of pretreatment system, filters, Cartridge Filters and pumps to replace the stagnant water inside filter(s) | Replacement with filtered raw water (fresh water) |
| 10. Wait for startup | If membranes shall be replaced for storage, Go to step 11, If not Go to step 9 |
| 11. Resanitize membranes with 0.5 wt % Formaldehyde, 250 mg/L Mg++ from MgCl2 |  |

| FLUSHING OF R.O MEMBRANES |  |
| --- | --- |
| JOB DESCRIPTION | REMARKS |
| Flushing Procedure I This procedure should be appliced only when flushing sterilization solution, such as when cleaning a new membrane. There are separate proce-dures for B-9 and B-10 Permeators, as shown in the Table on next page | The Permeators shall be flushed with flushing water of TDS less than 5,000 mg/L before and after the following : - CLEANING - POST-TREATMENT - STERILIZATION |
| Flushing Procedure II This procedure should be applied in the following cases : - Before Cleaning | There are four (4) different procedures which may be applied. The flushing procedure to be applied depends on whether the Permeator is being Cleaned, Post-treated or Sterilized, and whether the flush is being performed before or after the above treatment |
| - Prior to PT-A and PT-B Post-treatment - Prior to Sterilization Flushing Procedure III | CAUTION: The cleaning flush procedure may be different than the Post-treatment flush procedure. Always refer to the following table for the proper flushing procedure to followed. The Table shows the pressures, flow rates and treatment times for each procedure |
| This procedure should be applied in the following cases : |  |
| - In-between successive Cleanings |  |
| - At the end of Cleaning |  |
| - At the end of PT-A or PT-B Post-treatment |  |
| Flushing Procedure IV |  |
| This procedure should be applied only in case of flushing after Citric Acid cleaning. |  |

| REGULAR SERVICING & MAINTENANCE JOBS |  |  |
| --- | --- | --- |
| JOB DESCRIPTION | REMARKS | INTERVAL OR CRITERIA |
| CARTRIDGE FILTER |  |  |
| 1. Change Cartridge |  | 30 Days or at p>100 kPa |
| pH MONITOR |  |  |
| 1. Calibrate using standard buffer solution |  | 7 Days |
| MEMBRANE CLEANING | Failure to recognize that some form of failure is taking place and to initiate cleaning is the most common reason Permeators are destroyed fouling if recognized in time, can be stopped and system performance restored | 3 Months |
| LUBRICATE BEARINGS ON CENTRIFUGAL PUMP |  | 3 Months |
| 1. Check guand packing, shift sleeves, Gaskets etc. for any sign of deterioration |  | 1 Year |
| CALIBRATION OF GAUGES |  | 3 Months |
| AIR COMPRESSOR |  |  |
| 1. Clean Air Filter |  | 1 Week |
| 2. Replace Air Filter |  | 1 Year |
|  | (Continue next page) |  |

| REGULAR SERVICING & MAINTENANCE JOBS |  |  |
| --- | --- | --- |
| JOB DESCRIPTION | REMARKS | INTERVAL OR CRITERIA |
| (Cont’d) |  |  |
| ELECTRICAL EQUIPMENT |  |  |
| 1. Check adjustment and the operation of the protection devices (thermal, magnetic) |  | 1 Month |
| 2. Check time delay adjustments |  | 1 Year |
| 3. Tighten the connection |  | 1 Year |