## RO calculations (2)
Salt Rejection %
Salt Passage %
Recovery % |  |  |  | Prepared by /Dr. Mohamed Shaltout
Concentration Factor
Flux
Mass Balance
1 gallon = 4.54 litter
feed water flow | 1000 | GPM
feed water conductivity | 1000 | uS
permeate water flow | 850 | GPM
permeate water conductivity | 10 | uS
reject water flow | 100 | GPM
reject water conductivity | 9000 | uS
number of membrains | 10
area of each membrain | 365 | SQ FT
Salt Rejection % | 99
Salt Passage % | 1
Recovery % | 85
Concentration Factor | 6.6667
Flux | 335.3425 | GFd
left Mass | 1000000
right mass | 908500
Mass balance% | 4.7943
Note on A1: shaltout: The higher the salt rejection, the better the system is performing. A low salt rejection can mean that the membranes require cleaning or replacement.
Note on A4: shaltout: This is the amount of salts expressed as a percentage that are passing through the RO system. The lower the salt passage, the better the system is performing. A high salt passage can mean that the membranes require cleaning or replacement.
Note on A6: shaltout: Percent Recovery is the amount of water that is not sent to drain as concentrate, but rather collected as permeate or product water. The higher the recovery % means that you are sending less water to drain as concentrate and saving more permeate water. However, if the recovery % is too high for the RO design then it can lead to larger problems due to scaling and fouling
Note on A11: shaltout: The concentration factor is related to the RO system recovery and is an important equation for RO system design. The more water you recover as permeate (the higher the % recovery), the more concentrated salts and contaminants you collect in the concentrate stream
Note on A14: shaltout: This means that number of gallons of water is passed through each square foot of each RO membrane per day. This number could be good or bad depending on the type of feed water chemistry and system design
Note on A26: shaltout: A Mass Balance equation is used to help determine if your flow and quality instrumentation is reading properly or requires calibration. If your instrumentation is not reading correctly, then the performance data trending that you are collecting is useless A difference of +/‐ 5% is ok. A difference of +/‐ 5% to 10% is generally adequate. A difference of > +/‐ 10% is unacceptable and calibration of the RO instrumentation is required to ensure that you are collecting useful data. In the example above, the RO mass balance equation falls out of range and requires attention

## RO chemicals addition
RO chemicals addition |  |  |  |  | Prepared by /Dr. Mohamed Shaltout
Feed flow | 900 | m3/h
Chemical dosage | 17 | ppm
Available chemical concentration (purity) | 100 | %
Prepared chemical concentration | 20 | %
Prepared Solution density | 1.3
Selected pump capacity | 220 | L/h
Selected tank capacity | 100 | L
Daily chemicals consumption | 367.2 | Kg/d of | 100 | %
Daily dosage | 1412.3077 | L/d of | 20 | %
Dosage/h | 58.8462 | L/h of | 20 | %
Pump strok % | 26.7483
Tank retention Time | 0.070806 | day(s)

## Filter design
Filters design |  |  |  | Prepared by : Dr. Mohamed Shaltout
Feed water flow rate required by (m3/h) | 1080 | m3/h
Designed Filteration Flow (from the following table) (m/h) | 12 | m/h
Designed Filteration Flow (gpm /ft2) | 4.9587 | gpm /ft2
Required Filteration Area by (m2 ) | 90 | m2
Required Filteration Diameter (D) incase of Circle Filter (m) | 10.7075 | m
Required Filteration Diameter (D) incase of Circle Filter (ft) | 35.1295 | ft
Required Filteration Diameter (D) incase of Circle Filter (inch) | 421.5527 | inch
Required Filteration Diameter (D) incase of Circle Filter (cm) | 1070.7459 | cm
Bed Depth |  | mm
Stander Fiber Filters
|  |  | Diameter by inch | Hight by inch
|  |  | D | H
|  |  | 8 | 44
|  |  | 10 | 54
|  |  | 13 | 54
|  |  | 16 | 65
|  |  | 18 | 65
|  |  | 21 | 65
|  |  | 24 | 72
|  |  | 30 | 72
|  |  | 48 | 72

## LSI
LSI
| pH | 7.28
| AF | 2.2
| CF | 1.7
| TF | 0.4
| LSI | -0.52

## conversion (hidden)
Hardness & Alkalinity convertor |  |  | BWADC
data
UK/Egypt units |  |  |  | Ca2+ | Mg2+
total hardness | 127 | mg/l CaCO3 |  | 31 | 13.6 | mg/l | data: | Damanhour treated water
[7 empty] | period | 2001-07-01 | 2002-02-28
alkalinity | #REF! | mg/l CaCO3
Ca-hardness | #REF! | mg/l CaCO3
EC | #REF! | µS/cm
results (input for calculation)
Netherlands units |  |  |  | Ca2+ | Mg2+ | total
Ca2+ + Mg2+ | 1.2689 | mmol/l |  | 0.77345 | 0.55967 | 1.3331 | mmol/l | 105.1%
| 7.1056 | °D
bicarbonate | #REF! | mmol/l |  | #REF! | Ca2+/HCO3- | (normal value 0,5)
| #REF! | mg/l
Ca2+ | #REF! | mg/l
EC | #REF! | mS/m

## calculation (hidden)
Calcium-Carbondioxyde-equilibrium |  |  | CaCO2-eq
|  | red : | data
Data |  | blue : | results
mol. weight
Ca (mg/l) | #REF! | 40.08 | Ca (mmol/l) | #REF!
HCO3(mg/l) | #REF! | 61.018 | HCO3(mmol/l) | #REF!
pH (-) | #REF!
Temp (°C ) | #REF! |  | T (K) | #REF! |  | calc. CO2eq | #REF! | #REF! | #REF! | #REF!
K2O (mS/m) | #REF! |  |  |  |  | calc. I2 | #REF! | calc. R1 | #REF!
CO2 (mg/l) | #REF! | 44.01 | CO2 (mmol/l) | #REF! |  | calc. pK1 | #REF! | #REF! | #REF! | #REF!
[6 empty] | calc. pK2 | #REF! | #REF!
Calculation constants | [5 empty] | calc. pKs old | #REF!
[6 empty] | calc. pKs new | #REF!
CO2eq (mmol/l) | #REF! |  |  |  |  | pK2-pKsRey | #REF!
pK1 | #REF! |  |  |  |  | calc. pHs | #REF! | #REF!
pK2 | #REF!
pKs(new) | #REF!
check
Calculated | (mmol/l) | (mg/l)
values
CO2 | #REF! | #REF!
pH | #REF!
pHs | #REF!
SI | guidelines | 0<SI<+0,3 | #REF!
Cu sol capac |  | < 3 mg/l | #REF! | Formula 1 | (formula not based on sulphate)
Pb sol capac |  | < 200 ug/l | #REF!
============ | =========== | =========== | =========== | =========== | ===========
Modification | 30-11-1988
Cl (mg/l) | #REF! |  | Cl (mmol/l) | #REF!
SO4 (mg/l) | #REF! |  | SO4(mmol/l) | #REF!
TAC(mmol/l) | bij pH<8,3 |  | #REF!
Cu sol capac |  | < 3 mg/l | #REF! | Formula 2 | KIWA notification 100
([Cl]+2[SO4])/TAC |  | < 1 (cast iron) | #REF!
============ | =========== | =========== | =========== | =========== | ===========
Modification | 01-08-1993
Cu sol capac |  | < 3 mg/l | #REF! | Formula 3 | LTPR-002
new pipes (0 to 3 years)

## INFO (hidden)
Witteveen+Bos Consulting Engineers
author | Peter Hiemstra M.Sc.
version | may 27, 1999
street | Van Twickelostraat 2
P.O. Box 233
city | 7400 AE Deventer
country | The Netherlands
telephone | +31 570 69 72 07
telefax | +31 570 69 73 44
e-mail | p.hiemstra@witbo.nl
website | http://www.witteveenbos.nl | (English version)
Commitment and quality
In 1946, Witteveen+Bos was established as a firm of consult-
ing engineers in the Netherlands. Since then, the company has
developed and expanded. Today, there are over 600 employees,
many of whom are shareholders in the fully employee-owned
company. We at Witteveen+Bos are committed to our work and
to the success of our company. This is a benefit to our clients
and an added value that distinguishes Witteveen+Bos.
Our company has a wide range of specialists, covering the
scope and depth of expertise needed to implement projects in
water, infrastructure, environment and construction. We strive
for a balance in our staff of experienced and young specialists,
all highly trained and dedicated. The full range of expertise is
available to provide comprehensive services for all phases in a
project - from developing the initial concept to after sales ser-
vices.
All services and products are based on the procedures and
regulations set down in the Witteveen+Bos quality system con-
forming to ISO-NEN-9001, certified by Lloyds Register Quality
Assurance.
operating worldwide
Witteveen+Bos is one of the leading consulting firms in the
Netherlands. As a completely independant private company,
Witteveen+Bos serves clients in both the public and private
sectors. Our clients include multilateral and bilateral donors,
ministries, provincial and local governments, industrial and
commercial companies, contractors, project developers and
research institutes. In line with our commitment to work closely
with clients, projects are undertaken from our offices nearby
our clients or even within a client's organisation.
Witteveen+Bos operates worldwide with branch offices and
affiliated companies in various countries around the world. We
have strategic alliances and joint operations with other consul-
tants operating internationally. Co-operation with national con-
sultants is actively sought in the countries where we work. In
some cases, permanent working arrangements are established,
while in other cases, arrangements are made on a project for
project basis.
international experience
Abu Dhabi, Algeria, Aruba, Bahrain, Bangladesh, Belgium,
Bosnia-Herzegovina, Brunei, Cape Verde Islands, China,
Columbia, Cyprus, Denmark, Dubai, Egypt, Finland, France,
Gaza, Germany, Ghana, Greece, India, Indonesia, Iran, Ireland,
Italy, Jamaica, Kuwait, Latvia, Lebanon, Luxembourg, Malaysia,
Mexico, Morocco, Netherlands Antilles, Nigeria, Norway,
Pakistan, Peru, Poland, Russian Federation, Slovakia, Slovenia,
Spain, Sri Lanka, Suriname, Czech Republic, Taiwan, Turkey,
United Kingdom, Ukraine, Vietnam, Zambia.
Witteveen+Bos advices on water :
* groundwater, surface water, water ecology, organization and
management, integral water management
* abstraction, purification and distribution of drinking water
* abstraction, treatment and distribution of household drinking water
* transport and purification of household and industrial waste
water, sludge processing
* strategy and policy, legislation and licensing
* information technology and process automation

## SDI
Silt denisty index
T | 15 | min.
ti | 20 | sec.
tf | 23 | sec.
SDI(t) | 0.86957
Prepared by /Dr. Mohamed Shaltout
Note on A7: shaltout: The Silt Density Index (SDI) can serve as a useful indication of the quantity of particulate matter in water and correlates with the fouling tendency of RO/NF systems. The SDI is calculated from the rate of plugging of a 0.45 µm membrane filter when water is passed through at a constant applied gauge pressure SDI is sometimes referred to as the Fouling Index (FI) The guideline is to maintain SDI15 at 5. To minimize the fouling, however, SDI 15 at <3 is recommended. A number of pretreatment technologies have proven effective in SDI reduction, including media filtration (such as sand/anthracite), ultrafiltration and cross-flow microfiltration. Polyelectrolyte addition ahead of filtration sometimes improves SDI reduction.

## Tubes Follow rate
Tubes Follow rate |  | Prepared by /Dr. Mohamed Shaltout
Tube diameter by inch | 2
Tube average flow | 9
Tube max flow | 11.7
Design flow for tube | 10.35

## ion excahnge for total hardness
ion excahnge for total hardness removal |  |  |  | Stander fiber sand filters
Water flow rate m3/h | 6 |  |  | Filter volume | Diameter by inch | Hight by inch
Total hardness ppm | 120 |  |  | Volume by L | D | H
Resin volume (L) | 314.1818 |  |  | 5.6148 | 8 | 44
Pressure vessel (inch) |  |  |  | 10.7671 | 10 | 54 | Clack WS1
Head control |  |  |  | 18.1963 | 13 | 54
Brin weight (kg) | 43.9855 | water volume for desolving salt (3 times brin weight) | 131.9564 | 25.4023 | 14 | 65
Bed volume (flow by (l/h)/resin volume (L) | 19.0972 | Crateria | 5:40 | 33.1785 | 16 | 65
|  |  |  | 41.9915 | 18 | 65 | Clack WS1.5
Prepared by /Dr. Mohamed Shaltout |  |  |  | 57.1551 | 21 | 65
|  |  |  | 82.691 | 24 | 72
|  |  |  | 129.2047 | 30 | 72
|  |  |  | 330.7641 | 48 | 72 | Clack WS2

## RO calculations
Salt Rejection %
Salt Passage %
Recovery % |  |  |  | Prepared by /Dr. Mohamed Shaltout
Concentration Factor
Flux
Mass Balance
1 gallon = 4.54 litter
feed water flow | 1000 | GPM
feed water conductivity | 1000 | uS
permeate water flow | 850 | GPM
permeate water conductivity | 10 | uS
reject water flow | 100 | GPM
reject water conductivity | 9000 | uS
number of membrains | 10
area of each membrain | 365 | SQ FT
Salt Rejection % | 99
Salt Passage % | 1
Recovery % | 85
Concentration Factor | 6.6667
Flux | 335.3425 | GFd
left Mass | 1000000
right mass | 908500
Mass balance% | 4.7943
Note on A1: shaltout: The higher the salt rejection, the better the system is performing. A low salt rejection can mean that the membranes require cleaning or replacement.
Note on A4: shaltout: This is the amount of salts expressed as a percentage that are passing through the RO system. The lower the salt passage, the better the system is performing. A high salt passage can mean that the membranes require cleaning or replacement.
Note on A6: shaltout: Percent Recovery is the amount of water that is not sent to drain as concentrate, but rather collected as permeate or product water. The higher the recovery % means that you are sending less water to drain as concentrate and saving more permeate water. However, if the recovery % is too high for the RO design then it can lead to larger problems due to scaling and fouling
Note on A11: shaltout: The concentration factor is related to the RO system recovery and is an important equation for RO system design. The more water you recover as permeate (the higher the % recovery), the more concentrated salts and contaminants you collect in the concentrate stream
Note on A14: shaltout: This means that number of gallons of water is passed through each square foot of each RO membrane per day. This number could be good or bad depending on the type of feed water chemistry and system design
Note on A26: shaltout: A Mass Balance equation is used to help determine if your flow and quality instrumentation is reading properly or requires calibration. If your instrumentation is not reading correctly, then the performance data trending that you are collecting is useless A difference of +/‐ 5% is ok. A difference of +/‐ 5% to 10% is generally adequate. A difference of > +/‐ 10% is unacceptable and calibration of the RO instrumentation is required to ensure that you are collecting useful data. In the example above, the RO mass balance equation falls out of range and requires attention