## Sheet2
WATER HAMMER ANALYSIS
INPUT: | Dischrge |  | Q(in cu.m) | = | 0.294
| Diameter of pipe |  | D (in m) | = | 0.5
| Time of concentratiopn |  | t (sec) | = | 1
| Length of pipe |  | L (in m) | = | 2500
| rigidity modulus |  | K (N/m2) | = | 1960000000
| Youngs modulus |  | E (N/m2) | = | 191000000000
| deformation |  | d (cm) | = | 0.01
| density |  | ρ (Kg/m3) | = | 1000
| nature of pipe |  |  | = | elastic
SOLUTION:
STEP 1: | Calculation of the area of pipe |  | A= | πD2/4
|  |  | A= | 0.19625 | sq.m
STEP 2: | Calculate velocity of flow |  | V= | Q/A
|  |  | V= | 1.4981 | m/s
STEP 3: | Calculate celsity |  | c= | (K/ρ)0.5
|  |  | c= | 1400
STEP 4: | Calculation o critical time |  | T= | 2L/c
|  |  | T= | 3.5714 | sec
STEP 5: | Calculate pressure force
| ;If (t>T) then gradual closer : |  | gradual closer |  | P=ρLV/D
|  |  |  | P= | 7490445.8599 | N/sq.m
| ;If (t<T) then sudden closer : |  | sudden closer |  | a) for rigid pipe: P= |  | ρcV
[6 empty] | P= | 2097324.8408 | N/sq.m
[5 empty] | b) for elastic pipe P= |  | (ρ/(1/K+D/dE))0.5
[5 empty] | where; | 1/k= | 5.102e-10 |  | trail 01 | rigid
[6 empty] | D/dE= | 2.6178e-10 |  | trail 02 | 1138140.2909
[5 empty] | therefore; | P= | 1138140.2909 | N/sq.m
| ANSWER; | Condition: | sudden closer
|  | Pipe type: | elastic
|  | Pressure: | 1138140.2909 | N/sq.m