## Sheet1
Multi-Media Filter (Vertical ) | [5 empty] | نسألكم الدعاء بظاهر الغيب . أخوكم م محمد عبدالعال |  |  |  | 2600 | 2600 | 1800 | 1600
[8 empty] | 2600 | mm | 2600 | 2600 | 1800 | 1600
RO Permeate | m3/hr | 60 | 41 | 41 | 41 |  |  |  |  | 2600 | 2600 | 1800 | 1600
RO Recovery | % | 50 | 52 | 52 | 52 |  |  |  |  | 2600 | 2600 | 1800 | 1600
Total Number of filters | Ea | 2 | 1 | 2 | 2 |  |  |  |  | 2600 | 2600 | 1800 | 1600
[10 empty] | 2600 | 2600 | 1800 | 1800
|  | Open intake | Normal SDI | SDI<3 | SDI<2 |  |  |  |  | 2600 | 2600 | 2000 | 2000
Designed Filteration Flow | gpm /ft2 | 5 | 6 | 7 | 8 |  |  |  |  | 2600 | 2600 | 2200 | 2200
Designed Filteration Flow | m3/hr.m2 | 12.2224 | 14.6669 | 17.1114 | 19.5559
Feed Flow | m3/hr | 120 | 78.8462 | 78.8462 | 78.8462 |  |  |  |  | 2600 | 2600 | 2400 | 2400
Feed Flow per each MMF | m3/hr | 60 | 78.8462 | 39.4231 | 39.4231 |  |  |  |  | 2600 | 2600 | 2600 | 2600
Feed Flow per each MMF | gpm | 264.172 | 347.1491 | 173.5746 | 173.5746 |  |  |  |  | 2800 | 2800 | 2800 | 2800
Required Filteration Area | ft2 | 52.8344 | 57.8582 | 24.7964 | 21.6968 |  |  |  |  | 3000 | 3000 | 3000 | 3000
Required Filteration Area | m2 | 4.909 | 5.3758 | 2.3039 | 2.0159 |  |  |  |  | Add More MMF | Add More MMF | Use Two MMF | Use Two MMF
Filter Diameter | ft | 8.204 | 8.5851 | 5.6203 | 5.2573
Filter Diameter | Cm | 250.0703 | 261.6894 | 171.316 | 160.2514 |  |  | 1200
Net Diameter | Cm | 250.0703 | 261.6894 | 171.316 | 160.2514
Net Diameter (Selection ) | mm | 2600 | 2600 | 1800 | 1600
The Selected Diameter |  | 2600
Media Distribution In mm | B (mm) | Free Zone | Anthracite | Sand 0.7:1.2 | Gv 3:6 | Gv 6:9 | Gv 9:12 | Gv 12:18
| 1200 | 285 | 75 | 480 | 72 | 72 | 72 | 144 |  | 1200
Volume |  | 1.5124 | 0.398 | 2.5472 | 0.38208 | 0.38208 | 0.38208 | 0.76415
Kg |  | 0 | 310.4361 | 4075.4688 | 649.5278 | 706.8391 | 706.8391 | 1375.4707
Number Of MMF In BW same time |  | 1
Designed BW flow | gpm/ft2 | 10 | 11 | 12 | 15
Designed BW flow | m3/hr.m2 | 24.4451 | 26.8896 | 29.3341 | 36.6676
Actual MMF area | m2 | 5.3066 | 5.3066 | 5.3066 | 5.3066
Bachwash flow rate | gpm | 571.1976 | 628.3174 | 685.4371 | 856.7964
Bachwash flow rate | m3/hr | 129.7203 | 142.6924 | 155.6644 | 194.5805
Bachwash Time | Minutes | 10 | 10 | 10 | 10
Backwash volume | m3 | 21.6201 | 23.7821 | 25.9441 | 32.4301
Over estimate Feed Flow | m3/hr | 0.90084 | 0.99092 | 1.081 | 1.3513 | MMF surface Area can loaded by this value
Total Feed Flow Per MMF | m3/hr | 60.9008 | 79.837 | 40.5041 | 40.7743
Total System Feed Flow | m3/hr | 121.8016 | 79.837 | 81.0081 | 81.5486
No of filter feed pumps in Service | Ea | 1
Filter Feed Pump Selection | m3/hr | 121.8016 | Bar | 4
B/W Pump Selection | m3/hr | 155.6644 | Bar | 3
Backwash tank Volume | m3 | 28.5385 | If we use it in rains | 57.077
Cartridge Filter 5 Um Length | Inch | 40
No of Cartridge Filter 5 Um Elements | Ea | 36.6946