## BS 2486-1997
BRITISH STANDARD - Recommendations for treatment of water for steam boilers and water heaters | [5 empty] | ICS 13.060.01;91.140.65
Water treatment for hot water systems
System type | Low and medium temperature hot water systems up to 120°C |  |  | Hot temperature hot water systems above 120°C
Materials of constructions (galv.steel isn't allowed) | Fe only | Fe with Cu and Cu alloys | Fe with Cu, Cu alloys and Al | Fe only | Fe with Cu and Cu alloys | Fe with Cu, Cu alloys and Al
Water quality | Raw water | Raw water | Raw water (Al present hard water don't allowed) | Raw water (anions-Cl,SO4<10mg/kg) | Raw water (anions-Cl,SO4<10mg/kg) | Raw water (anions- Cl,SO4<10mg/kg; Al present hard water don't allowed)
pH limits | 8.0 to 10.5 | 7.2 to 9.2 | 7.0 to 8.0 | 8.0 to 10.5 | 7.2 to 9.2 | 7.0 to 8.0
Alkalinity control | NaOH | NaOH | Untreated or buffered | NaOH or amines | NaOH or amines | Amines
Cu corrosion inhibitor | none | Benzotriazole / tolyltriazole | Benzotriazole / tolyltriazole | none | Benzotriazole / tolyltriazole | Benzotriazole / tolyltriazole
Oxygen scavenger and/or | Na-sulfite, tannin, hydrazine or DEHA | Na-sulfite, tannin, hydrazine or DEHA | Na-sulfite, tannin, hydrazine or DEHA | Volatile oxygen scavenger | Volatile oxygen scavenger | Volatile oxygen scavenger
Corrosion inhibitor | Suitable inhibitor blend (not chromate) | Suitable inhibitor blend (not chromate) | Suitable inhibitor blend (not chromate)
Sludge conditioner | Suitable organic polymer or blend | Suitable organic polymer or blend | Suitable organic polymer or blend | Suitable organic polymer or blend | Suitable organic polymer or blend | Suitable organic polymer or blend
Recommended water charasteriscics for shell boilers up to 30 bar
Parameters | Units | Values
FEED WATER
Appearance |  | Clear, produces no stable foam
pH value at 25°C | - | 8.5 to 9.5
Total hardness | mg/kg CaCO3 | 2 max.
Dissolved oxygen | mg/kg CaCO3 | as low as possible
Total alkalinity to pH 4.5 | mg/kg CaCO3 | <25
Oil and grease | mg/kg CaCO3 | 1 max.
BOILER WATER
Heat flux | kW/m2 | below or equal 300 | above 300
pH value at 25°C | - | 10.5 to 12.0 | 9.5 to 10.5
Total alkalinity to pH 4.5 | mg/kg CaCO3 | 1000 max. | 100 max.
Caustic alkalinity | mg/kg CaCO3 | 350 min. | 20 min.
Oxygen scavenger
Na-sulfite | mg/kg | 30 to 70
Hydrazine | mg/kg | 0.1 to 1.0 | 0.1 to 1.0
Tannin | mg/kg | 120 to 160
Iso ascorbic acid | mg/kg | 15 to 30
DEHA | mg/kg | 0.1 to 1.0 in FW | 0.1 to 1.0 in FW
Phosphate | mg/kg PO4 | 30 to 60 | 10 to 30
Silica | mg/kg SiO2 | 150 max. | 5 max.
Suspended solids | mg/kg | 200 max. | 20 max.
Dissolved solids | mg/kg | 3500 max. | 1000 max.
Conductivity at 25°C | mikroS/cm | 7000 max. | 2000 max.
Recommended water charasteriscics for fired water tube boilers
P (bar) at boiler outlet | 0-20 | 21-40 | 41-60 | 61-80 | 81-100 | 101-120 | >121
FEED WATER AT ECONOMIZER INLET
Total hardness mg/kg CaCO3 max. | 2 | 1 | not decectable | not decectable | not decectable | not decectable | not decectable
pH value at 25°C | 8.5 to 9.5 | 8.5 to 9.5 | 8.5 to 9.5 | 8.5 to 9.5 | 8.5 to 9.5 | 8.5 to 9.5 | 8.5 to 9.5
Oxygen, mg/kg as O2 max. | 0.02 | 0.02 | 0.01 | 0.005 | 0.005 | 0.005 | 0.005
Fe, Cu, Ni mg/kg max. | 0.05 | 0.05 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02
Total solids, alk, Si | The level of solids in FW depends on the lewel of blowdown required to maintain the specified boiler water conditions. (attemp.: <1 mg/kg)
Organic carbon | as low as possible | as low as possible | as low as possible | as low as possible | as low as possible | as low as possible | as low as possible
BOILER WATER
Phosphate mg/kg PO4 | 30 to 70 | 20 to 50 | 20 to 40 | 15 to 30 | 10 to 20 | 3 to 10 | 3 to 5
NaOH alk. mg/kg CaCO3 | 50 to 300 | 50 to 150 | 25 to 50 | 10 to 20 | 5 to 10 | 2 to 5 | 1 to 5
Si as mg/kg SiO2 | < 0.4 x NaOH alk. | < 0.4 x NaOH alk. | 20 max. | 5 max. | 2 max. | 1.5 max. | 0.5 max.
Sulfite as mg/kg Na2SO3 | 30 to 50 | 20 to 40 | 15 to 20 | not recommended | not recommended | not recommended | not recommended
Hydrazine as mg/kg N2H4 | 0.1 to 1.0 | 0.1 to 0.5 | 0.1 to 0.2 | 0.05 to 0.1 | 0.05 to 0.1 | 0.05 to 0.1 | 0.05 to 0.1
DEHA as mg/kg | 0.1 to 0.25 in FW | 0.1 to 0.25 in FW | 0.1 to 0.25 in FW | 0.1 to 0.25 in FW | 0.1 to 0.25 in FW | 0.1 to 0.25 in FW | 0.1 to 0.25 in FW
Tannin as mg/kg | 120 to 160 | not recommended | not recommended | not recommended | not recommended | not recommended | not recommended
Iso ascorbic acid, mg/kg | 15 to 30 | 15 to 30 | 15 to 30 | not recommended | not recommended | not recommended | not recommended
Chloride mg/kg Cl | - | - | -
NVAT (coal fired) |  |  |  | < 8 | < 4 | < 2 | < 2
NVAT (oil fired) |  |  |  | < 8 | < 4 | < 0.5 | < 0.5
AVT (coal fired) |  |  |  | < 0.02 | < 0.2 | < 0.2 | < 0.2
AVT (oil fired) |  |  |  | < 0.02 | < 0.2 | not recommended | not recommended
Dissolved solids mg/kg | 3000 | 2500 | 1000 | 200 | 50 | 20 | 10
Conductivity at 25°C mikro S/cm | 6000 | 5000 | 2000 | 450 | 150 | 60 | 35
Recommended water charasteriscics for non-fired water tube boilers (e.g. combined cycle plant and combined heat and power plant)
P (bar) at boiler outlet | 0 to 40 | 41 to 80 | Above 80
FEED WATER AT ECONOMIZER INLET
Total hardness mg/kg CaCO3 max. | not detectable | not detectable | not detectable
pH value at 25°C | 9.3 to 9.8 | 9.3 to 9.8 | 9.3 to 9.8
Oxygen, mg/kg as O2 max. (before ox. scav.) | 0.02 | 0.01 | 0.005
Fe, Cu, Ni mg/kg max. | 0.05 | 0.03 | 0.02
BOILER WATER
Phosphate mg/kg PO4 | 20 to 40 | 15 to 30 | 3 to 10
NaOH alk. mg/kg CaCO3 | 25 to 50 | 10 to 50 | 2 to 5
Si as mg/kg SiO2 | 20 | 5 | 1 to 5
Oxygen scavengers
Sulfite as mg/kg Na2SO3 | 15 to 20 | - | -
Hydrazine as mg/kg N2H4 | 0.1 to 0.5 | 0.05 to 0.1 | 0.05 to 0.1
DEHA as mg/kg | 0.1 to 0.25 in FW | 0.1 to 0.25 in FW | 0.1 to 0.25 in FW
Tannin as mg/kg | 120 to 160 | not recommended | not recommended
Iso ascorbic acid, mg/kg | 15 to 30 | 15 to 30 | not recommended
Dissolved solids mg/kg | 1000 | 200 | 50
Conductivity at 25°C mikro S/cm | 2000 | 400 | 100
Recommended water charasteriscics for feed water at economizer inlet for once-through boilers
Parameters | Units | Values
Cation conductivity at 25°C | mikroS/cm | 0.2 max.
Oxygen (after deaerator) | mg/kg O2 | 0.005 max.
Silica | mg/kg SiO2 | 0.02 max.
Iron | mg/kg Fe | 0.01 max.
Copper and nickel | mg/kg Cu + Ni | 0.005 max.
pH (for Cu alloys) |  | 9.2 to 9.5 (8.5 to 9.2)
Start up/load change weighted mean iron | mg/kg Fe | 0.1 max.
Start up/load change weighted mean Cu and Ni | mg/kg Cu + Ni | 0.03 max.