## W.Demand
Calculation of Water Demand
| Expected Population after |  | 30 | = | 61400
| Average Rate of Water Supply / Capita |  |  | = | 135
| Water required for above purposes for whole town = | [5 empty] | ( 61400 x 135 )
[6 empty] | = | 8.289
| Industrial Demand |  |  |  |  | = | 0.6
Fire Requirement :
It can be assumed that city is a residential town ( Low Rise Buildings )
| Water for Fire |  |  |  | MLD
|  | 100 | 61.4 | 10 | -3 | 0.78
| Average Daily Draft = |  | ( 8.289 + 0.6 ) = |  |  | 8.889
| Maximum Daily Draft = |  | ( 1.5 x 8.889 ) = |  |  | 13.334
Coincident Draft = Maximum Daily Draft + Fire Demand
|  | = ( 13.334 + 0.78 ) = |  |  | 14.114
( Considering Draft < Maximum Hourly Draft )
Design Capacity For Various Components
| Intake Structure Daily Draft = |  | 13.334
| Pipe Main = Maximum Daily Draft = |  |  | 13.334
Filters and Other Units at Treatment Plant : |  |  |  | = | 2
|  |  |  | = | ( 2 x 8.889 ) = |  |  | 17.778
| Lift Pump : |  |  | = | 2
|  |  |  | = | ( 2 x 8.889 ) = |  |  | 17.778

## Water Standards
Physical & Chemical Standards Of Water
S.No. | Characteristics | Acceptable |  | Cause for Rejection
1 | Turbidity ( Units on J.T.U. Scale ) | 2.5 |  | 10
2 | Colour ( Units on Platinum Cobalt Scale ) | 5 |  | 25
3 | Taste & Odour | Unobjectionable |  | Unobjectionable
4 | PH | 7 | 8.5 | 6.5 | 9.2
5 | Total Dissolved Solids ( mg / L ) | 500 |  | 1500
6 | Total Hardness ( mg / L as Ca CO 3 ) | 200 |  | 600
7 | Chlorides ( mg / L as C 1 ) | 200 |  | 1000
8 | Sulphates ( mg / L as S O 4 ) | 200 |  | 400
9 | Fluorides ( mg / L as F ) | 1 |  | 1.5
10 | Nitrates ( mg / L as N O 3 ) | 45 |  | 45
11 | Calcium ( mg / L as Capacity ) | 75 |  | 200
12 | Magnesium ( mg / L as Mg ) | 30 |  | 150
13 | Iron ( mg / L as Fe ) | 0.1 |  | 1
14 | Manganese ( mg / L as M n ) | 0.05 |  | 0.5
15 | Copper ( mg / L as C u ) | 0.05 |  | 1.5
16 | Zinc ( mg / L as Z n ) | 5 |  | 15
17 | Phenolic Compounds ( mg / L as Phenol ) | 0.001 |  | 0.002
18 | Anionic Detergents ( mg / as MBAS ) | 0.2 |  | 1
19 | Mineral Oil ( mg / L ) | 0.01 |  | 0.3
TOXIC MATERIALS
20 | Arsenic ( mg / L as A s ) | 0.05 |  | 0.05
21 | Cadmium ( mg / L as Cd ) | 0.01 |  | 0.01
22 | Chromium ( mg / L as Hexavalent Cr ) | 0.05 |  | 0.05
23 | Cyanides ( mg / L as C ≡ N ) | 0.05 |  | 0.05
24 | Lead ( mg / L as P b ) | 0.1 |  | 0.1
25 | Selenium ( mg / L as Se ) | 0.01 |  | 0.01
26 | Mercury ( mg / L as Hg ) | 0.001 |  | 0.001
27 | Polynuclear Aromatic Hydrocarbons ( mg/L ) | 0.2 |  | 0.2
RADIO ACTIVITY
28 | Gross Alpha Activity in pico Curie ( ρ Ci / L ) | 3 |  | 3
29 | Gross Beta Activity ( ρ Ci / L ) | 30 |  | 30

## Comparision & Treatment
Comparison of Given Data & Standard Data and Treatment Proposed
S.No. | Particulars | Actual | Standard |  | Difference |  | Treatment Proposed
1 | pH | 7.5 | 7 | 8.5 | 0.25 | Hence OK. | Not Necessary
2 | Turbidity | 50 | 2.5 |  | 47.5 |  | Clarifier & Rapid Sand Filler
3 | Total Hardness | 550 | 200 |  | 350 |  | Softening
4 | Chlorides | 200 | 200 |  | 0 |  | -
5 | Iron | 2.5 | 0.1 |  | 2.4 |  | Aeration
6 | Manganese | 3.5 | 0.05 |  | 3.45 |  | Aeration
7 | Carbonate | 110 | 0 |  | 110 |  | Softening
8 | MPN | 3.5 | 0 |  | 3.5 |  | Chlorination

## Intake Design
Design of Intake Well
Design Criteria :
S.No. | Particulars |  |  | Values
1 | Detention Time / Period |  |  | 5 |  | 10
2 | Diameter of Well |  |  | 5 | 10 | ( Maximum = | 15
3 | Depth of Well |  |  | 4 |  | 10
4 | Velocity of Flow |  |  | 0.6 |  | 0.9
5 | Number of Units |  |  | 1 | 3 | ( Maximum = | 4
6 | Free Board |  |  |  | 5
Design Assumptions :
Given F.S.L. |  |  | = | 27
Minimum R.L. |  |  | = | 28
Given invert of gravity main |  |  | = | 24
Detention Time |  |  | = | 10
Design Calculations :
Flow of Water Required = |  |  | 13.334 |  | 3600 x 24
|  | = | 0.1543 | 3 / sec. |  |  |  |  | 13331.52
Volume of Well = |  |  | 0.1543 | 10 | 60
|  | = | 92.58 | ³ |  |  |  | 5554.8
Cross-sectional Area of Intake Well = |  |  |  | 92.58 | 4
|  |  | = | 23.145 | ²
Diameter of Intake Well = |  |  | 23.145 | 4
Π
|  | d = | 5.43 | < 10 m ( O.K. )
Hence Diameter of Intake Well = |  |  |  | 5.43 | ≡ | 5.5 m
Summary :
S.No. | Particulars |  |  | Values
1 | Number of Intake Wells |  |  | 1 Unit
2 | Diameter of Intake Well |  |  | 5.5 m
3 | Height of Wall |  |  | 4
4 | R.L. of bottom of Well |  |  | 24

## Pen Stock & Bell Mouth
Design of Pen Stock & Bell Mouth Strainer
a) | Pen Stock
These are the Pipes provided in Intake Well to allow water from water body to intake well. These pen stocks are provided at different levels, so as to take account of seasonal variation in water level (as H.F.L, W.L., L.W.L.). Trash racks of screens are provided to protect the entry sizeable things which can create trouble in the pen stock. At each level more than one pen stock is provided to take account of any obstruction during its operations. these pen stocks are regulated by valves provided at the top of intake wells.
b) | Design Criteria
| Velocity through Pen Stock |  |  |  | = | 0.6 | 1
| Diameter of each Pen Stock |  |  |  | = | 1
| Number of Pen Stock for each Intake Well |  |  |  | = | 2
c) | Design Calculation
| Number of Intake Well |  |  |  | = | 1
| Number of Pen Stock for each Level |  |  |  | = | 2
| Velocity |  |  |  | = | 0.75
| C / S area of each Pen Stock |  |  |  | = | 0.1543 / ( 0.75 x 2 )
[5 empty] | = | 0.103 | ²
| Diameter |  |  | 0.103 | = | 0.3622 | ≡ | 0.4
Π
d) | Summary
| S.No. | Particulars |  |  | Values
| 1 | Number of Pen Stock / Well |  |  | 2
| 2 | At Each Level |  |  | 1
| 3 | Diameter of Pen Stock |  |  | 0.4
Design of Bell Mouth Strainer :
a) | Design Criteria
| Velocity of Flow |  |  |  | = | 0.2 | 0.3
| Hole Diameter |  |  |  | = | 6 | 12
| Area of Strainer |  |  |  | = | 2
b) | Assumptions
| Velocity of Flow |  |  |  | = | 0.25
| Hole Diameter |  |  |  | = | 10
c) | Calculation
| Area of Each Hole = |  |  | ( 10 x 10 ) x | Π | 0.785 | ²
4
Area of Collection = Area of Pen Stock
| 0.1543 |  | 0.785
( 0.25 x 2 )
|  | N = | 0.1543 | 1 | = | 3931.2
|  |  | ( 0.25 x 2 ) | 0.785
| Area of Strainer = |  | 2
|  | = | 2 x 3931.2 x 0.785 |  | = | 6171.98
| Diameter of Bell Mouth Strainer = |  |  |  | Π | x d 2 | = | 6171.98 | ² | 88.6701
4
|  | Diameter = d = |  | ( 6171.98 x 4 ) |  | 88.67
Π
| Provide Diameter of |  | 0.9 | for Bell Mouth Strainer.
|  |  |  | Regulating Valves |  |  | Manhole
| F.S.L. = | 27
Bell Mouth Strainer
3
| L.W.L. = | 26
Gravity Main
5.5 m
Bottom R.L. = |  | 24
Section
Plan
²²

## Gravity Main
Design of Gravity Main
a) | Gravity Main
The Gravity Main connects the Intake Well to the Jack Well & water flows through it by gravity. To secure the greatest economy, the diameter of a single pipe through which water flows by gravity should be such that all the head available to cause flow is consumed by friction. The available fall from the intake well to the jack well & the ground profile in between should generally help to decide if a free flow conduit is feasible. once this is decided the material of the conduit is to be selected keeping in view the local cost & the nature of the terrain to be traversed. Even when a fall is available, a pumping or force main, independently or in combination with a gravity main could also be considered. Gravity pipelines should be laid below the hydraulic gradient.
b) | Design Criteria
| Diameter of Gravity Main |  |  |  |  | = | 0.3 | 1
| Velocity of Water |  |  |  |  | = | 0.6 | 0.9
| Number of Gravity Main = Number of Intake Well |  |  |  |  | = | 1
| Assumption Velocity |  |  |  |  | = | 0.7
c) | Design Calculation
| R.C.C. | Circular | Pipe is used. For this |  | n = | 0.013
| Conduit Velocity ( Assumed ) |  |  |  |  | = | 0.7
| Area of Conduit required |  |  | (A = Q / V ) |  | = | 0.1543 | 0.7
[6 empty] | = | 0.2204 | ²
| Diameter of the conduit » |  |  | Π | x d 2 | = | 0.2204 | ²
4
|  |  | Diameter = d = |  | 0.2204 x 4 |  | 0.5299 | ≡ | 0.55
Π
| Using Manning's Formula - | [12 empty] | 1.727
| » |  |  | 0.7 x 0.7 | x 0.013 x 0.013 |  |  | = | 0.0011668 |  |  |  | 857.0131
|  |  |  | ( 0.55 / 4 ) |  | 4/3
[8 empty] | = | 11.6684 | 10 | -4
[7 empty] | S = | 1 : | 857
| Here R = | Area | Π x D x D |  | 1 | = | D | = | 0.55
|  | Perimeter | 4 |  | Π x D |  | 4 |  | 4
| Head Loss = |  | 100 | 0.117
857
| R.L. of Gravity Main = |  |  | ( 27 - 3 ) = | 24
| R.L. of Gravity Main at Jack Well = |  |  |  | ( 24 - 0.117 ) = |  |  | 23.883
d) | Summary | [10 empty] | 3.12
| S.No. | Particulars |  |  | Values
| 1 | Number of Gravity Intake |  |  | 1
| 2 | Diameter of Gravity Intake |  |  | 0.55
| 3 | Invert Level at Intake Well |  |  | 24
| 4 | Invert Level at Jack Well |  |  | 23.883

## Jack Well
Design of Jack Well
a) | Jack Well
This structure serves as a collection of the sump well for the incoming water from the intake well from where the water is pumped through the rising main to the various treatment units.
The unit is more useful when number of intake wells are more than one, so that water is collected in one unit and then effected.
The Jack well is generally located away from the shore line, so that the installation of pumps, inspection maintenance is made easy.
b) | Design criteria
| Detention Time = |  | 0.5 | ( Detention time of intake Well ) |  |  |  | 3 | 15
|  | = | 0.5 | 10 | 5
| Suction Head = |  | 10
| Diameter of Well = |  | 20
c) | Design Calculations
| Detention Time = |  | 5
| Assuming Suction Head = |  |  | 8
| Bottom Clearance = |  | 1
| Top Clearance = |  | 0.5
Maximum depth of water that can be stored in condition when water is minimum in river .
| Minimum Depth of Water = |  |  | ( 26 - 22.883 ) = |  | 3.117
| Capacity of Well = |  |  | 0.1543 | 10 | 60 | 92.58 |  | ³
| C / S Area of Well = |  |  | 92.58 | 3.117 | 29.7 | ²
| Diameter of the Well » |  |  | Π | x d 2 | 29.7 | ²
4
|  | Diameter = d = |  | 29.7 x 4 | 6.15
Π
| R.L. of Bottom of Jack Well = |  |  | ( 23.883 - 1 ) = |  | 22.883
| R.L. of Bottom of Jack Well when full = |  |  |  | ( 22.883 + 7 ) = |  | 29.883
d) | Summary
| S.No. | Particulars |  |  | Values
| 1 | Diameter of Jack Well |  |  | 6.15
| 2 | R.L. of Bottom of Jack Well |  |  | 22.883
| 3 | R.L. of Top of Jack Well |  |  | 29.883
| 4 | Suction Depth |  |  | 2.12
| 5 | Top Clearance |  |  | 0.5
| 6 | Bottom Clearance |  |  | 1 |  |  |  |  | 4.88
| 7 | Head required ( h d ) |  |  | 4.88 |  | = ( 8 - 2.12 - 1 )

## Pumping Sys.
Design Of Pumping System
a) | Pumps
› | In the water treatment plant, pumps are used to boost the water from the jack well to the aeration units.
› | The following points are to be stressed upon :
→ | The suction pumping should be as short & straight as possible. It should not
| be greater than ( > ) |  | 10 | for centrifugal pump. |  |  | If head is more than 10 m ,
water is converted into vapour & thus inspite of creating water head, vapour
head is created & pump ceases to fuction.
→ | 2
→ | 2.5
The following four types of pumps are generally used -
i) | Buoyancy Operated pumps
ii) | Impulse Operated pumps
iii) | Positive Displacement Pumps
iv) | Velocity Adoptions pumps
The following criteria govern pump selection : -
♥ | Type of duty required.
♥ | Present & projected demand & pattern and change in demand.
♥ | The details of head & flow rate required.
♥ | Selecting the operating speed of the pump & suitable drive.
♥ | The efficiency of the pumps & consequent influence on power consumption and the
running costs.
b) | Diameter of Rising Main
| Discharge ( Q ) |  |  |  | = | 0.1543 | 3 / sec.
| Economical Diameter ( d ) |  |  |  | = | 0.97 | 1.22
[5 empty] | = | 0.97 | 1.22 | 0.1543
[5 empty] | = | 0.97 | 1.22 | 0.393
[5 empty] | = | 0.381 | 0.47946
| Hence Provide d = |  |  |  | = | 0.43023 | Say ≡ | 0.45
c) | Design Criteria
| Suction head should not be greater than |  |  |  |  | 10
| Velocity of flow length |  |  |  | = | 0.7 | 1.1
| Top Clearance |  |  |  | = | 0.5
| Bottom Clearance |  |  |  | = | 1
d) | Design Calculation
Frictional Losses in Rising Main -
| Velocity ( Assuming ) |  |  |  | = | 0.9
Head Loss | [5 empty] | 0.02 | 190 | 0.9 x 0.9 ) | 0.349
[6 empty] | 2 | 9.81 | 0.45
Here :
|  |  |  | f | = | 0.02
|  |  |  | L | = | 190
|  |  |  | g | = | 9.81
| Head Loss | » h f = | 0.349 | Say ≡ | 0.35
| Minor Losses should be assuming |  |  |  | = | 1
Hence Total Head of Pumping = ( h s + h d + h f + minor losses )
[5 empty] | = | ( 2.12 + 4.88 + 0.35 + 1 )
[5 empty] | = | 8.35
| Assuming | 2 |  | in Parallel is working
|  |  |  | 1000 | 0.1543 |  | 8.35 | 17.1787
[5 empty] | 75 |  |  |  |  | 1 | 0.735
|  |  |  | 17.1787 | = | 22.905 | Say ≡ | 25
|  |  |  | 0.75 | [5 empty] | 12.6264
|  |  |  | If ƞ | = | 75
e) | Summary
| S.No. | Particulars |  |  | Values
| 1 | Pumps Capacity |  |  | 25
| 2 | Diameter of Pipe |  |  | 0.45

## Rising Main
Design of Rising Main
a) | General
These are the pressure pipes used to convey the water from jack well to the treatment units.
The design of rising main is dependent on resistance to flow, available head, allowable velocities of flow, sediment transport, quality of water & relative cost.
Various types of pipes used are cast iron, steel, R.C.C, P.C.C, asbestos cement, polyethylene, rigid PVC, iron fibre glass pipe, glass reinforced plastic etc.
The determination of the suitability in all respects of the pipe of joints for any work is a matter of decision by the engineer concerned on the basis of requirements of the scheme.
b) | Design Criteria
| Permissible Velocity in Mains |  | = | 0.9 | 1.5
| Mains Diameter should be less than ( < ) of |  |  | 0.9
| Total Discharge in Mains |  | = | 0.1543 | 3 / sec.
c) | Design Calculations
| Economical Diameter ( d ) |  | = | 0.97 | 1.22
|  |  | = | 0.97 | 1.22 | 0.1543
|  |  | = | 0.97 | 1.22 | 0.393
|  |  | = | 0.381 | 0.47946
| Hence Provide d = |  | = | 0.43023 | Say ≡ | 0.45
d) | Summary
| S.No. | Particulars | Values
| 1 | Diameter of Mains Pipe | 0.45

## Aeration Unit
Treatment Units - Design Of Aeration Unit
Aeration unit
Aeration is necessary to promote the exchange of gases between the water & the atmosphere. In water treatment, aeration is practiced for three puposes :
i) | To add oxygen to water for imparting freshness, e.g. water from under ground sources devoid of or deficient in oxygen.
ii) | Expulsion of CO 2, H 2 S & other volatile substances causing taste and odour, e.g. water from deeper layers of an impounding reservoir.
iii) | To precipitate impurities like iron and manganese, in certain forms, e.g. water from some under ground sources.
The Concentration of gases in a liquid generally obeys Henry's Law which states that the concentration of each gas in water is directly proportional to the partial pressure or concentration of gas in the atmoshere in contact with water. The saturation concentration of a gas decreases with temperature & dissolved salts in water. Aeration tends to accelerate the gas exchange.
The three types of aerators are :
i) | Water Fall or Multiple Tray Aerators
ii) | Cascade Aerators
iii) | Diiffused Air Aerators
Design Criteria For Cascade Aerators
| Number of Trays |  |  |  | = | 4 | 9
| Spacing of trays |  |  |  | = | 0.3 | 0.75
| Height of the Structure |  |  |  | = | 2
| Space Requirement |  |  |  | = | 0.015 | 0.045 | 2 / m 3 / hr.
Design Calculations
| Disharge | ( Q max. ) |  |  | = | 0.1543 | 3 / sec.
| Provide Area at Tray |  |  |  | = | 17 | ²
| Diameter of bottom most tray |  |  |  | = | 5
| Rise of each Tray |  |  |  | = | 0.4
| Tread of each tray |  |  |  | = | 50 | 0.5
|  | ɸ 1 = | 1
| ɸ 2 = | 2 |  | R.L. |  | 31
ɸ 3 = | 3 |  |  | R.L. | 30.6
ɸ 4 = | 4 |  |  | R.L. |  | 30.2
ɸ 5 = | 5 |  |  |  |  | R.L. | 29.8
[6 empty] | R.L. | 29.4
[7 empty] | R.L. | 29
Inlet

## Alum Quantity
Design Of Chemical House & Calculation Of Chemical Dose
Alum Dose for Coagulation
The terms coagulation & flocculation are used indiscriminately to describe the process of removal of turbidity caused by the suspension colloids & organic colors.
The coagulant dose in the field should be judiciously controlled in the light of the jar test values. Alum is used as coagulant.
Design Criteria for Alum Dose
Alum required in particular season is given below :
|  | Monsoon |  | = | 50
|  | Winter |  | = | 20
|  | Summer |  | = | 5
Alum required
| Let the average dose of alum required be |  |  |  |  | 50 | 20 | 5 | in the
| Monsoon | Winter | Summer | seasons respectively.
Flow of Water Required Hourly = |  |  |  |  | 0.1543 | 60 | 60 | 555.48 | 3 / hour
Per day alum required for worst season for intermediate stage
|  |  |  | = | 50 | 555.48 | 1000 | 24
1000000
|  |  |  | = | 666.58 | Kg / Day
| 6 | months | 180 |  | ( 666.58 x 180 ) |  | 119984.4
| Number of Bags when 1 bag is containing = |  |  |  |  | 50
|  |  |  | = | 119984.4 |  | 2399.7 | Bags
50
|  |  |  | = | 2400
| 15 |  | each heep | = | ( 2400 / 15 ) = |  | 160 | no. of heeps |  | 160
| 0.2 |  |  | ² , | then total area required = |  |  | 32 | ²

## Lime-Soda Process
Lime - Soda Process
Softening
A water is said to be hard, when it does not form leather readily with soap. The hardness of
water is due to the presence of Calcium and Magnesium ions in most of the cases. The method
generally used are Lime-Soda process. Softening with these chemicals is used particularly for
water with high initial hardness |  |  |  | 500 |  |  | and suitable for water containing turbidity,
colour and iron salts. Lime -Soda softening con not reduce the hardness to value less | [9 empty] | 40
Design Criteria For Lime-Soda Process
| 30 | 200 |  | total hardness by this process.
Lime & Soda Required :-
→ Lime required for alkalinity.
| Molecular Weight of |  | Ca C O3 |  | = | 40 | 12 | 16 | 3
[5 empty] | = | 40 | 12 | 48 |  | 100
| Molecular Weight of |  | Ca O |  | = | 40 | 16 |  | 56
100 |  | Ca C O3 | alkalinity requires |  | = | 56 |  | Ca O
110 |  | Ca C O3 | alkalinity requires |  | = | ( 56 / 100 ) x 110
[5 empty] | = | 61.6 |  | Ca O
→ Lime required for Magnesium
Molecular Weight of Magnesium ( M n ) |  |  |  |  | = | 24
24 |  | Magnesium ( M n ) |  | requires | = | 56 |  | Ca O
1 |  | Magnesium ( M n ) |  | requires | = | ( 56 / 24 ) |  | mg / L of |  | Ca O
3.5 |  | Magnesium ( M n ) |  | requires | = | ( 56 / 24 ) x 3.5 |  | mg / L of |  | Ca O
[5 empty] | = | 8.2 | mg / L of |  | Ca O
| Hence, the total pure lime required |  |  |  | = | ( 61.6 + 8.2 ) = |  | 69.8
56 |  | of Pure Lime ( Ca O ) is equivalent to |  |  |  |  | 74 | of hydrated lime.
| Hence hydrated Lime is required |  |  |  | = | ( 69.8 x 74 ) / 56 = |  |  | 92.24
♥ | Soda ( Na 2 C O 3 )
Soda is required for non - carbonate hardness, as follows -
Molecular Weight of Soda ( Na 2 C O 3 ) |  |  |  |  | = | 11 | 12 | 16 | 3
[5 empty] | = | 22 | 12 | 48 |  | 82
100 |  | Non Carbonate Hardness ( NCH ) requires |  |  |  |  | 106 |  |  | Na 2 C O 3
| 61.6 |  | NCH requires |  | = | ( 106 / 100 ) x 61.6 = |  |  | 65.3 |  | Na 2 C O 3
| Total Quantity of Lime |  |  |  | = | 92.24 | 555.48 |  | 180 | 24 | 1000
1000000
[5 empty] | = | 221345.89
( One Bag contains = |  |  | 50
| Number of Bags required |  |  |  | = | 221345.89 |  | = | 4426.9 | 4427
50
| 15 |  | each heep |  | = | ( 4427 / 15 ) = |  | 295.1333 |  | no. of heeps
| 0.2 |  |  | ² , then total area required = |  |  |  | 59.03 |  | ²
Total Quantity of Soda required for 6 months |  |  |  |  | = | 65.3 | 555.48 |  | 180 | 24 | 1000
1000000
[5 empty] | = | 156698.69
| Number of Bags required |  |  |  | = | 156698.69 |  | = | 3134 | 3134
50
| 15 |  | each heep |  | = | ( 3134 / 15 ) = |  | 208.9333 |  | no. of heeps
| 0.2 |  |  | ² , then total area required = |  |  |  | 41.79 |  | ²
| Total Area for all Chemicals |  |  |  | = | ( 32 + 59.03 + 41.79 ) = |  |  |  | 132.82 |  | ²
30 |  | for chlorine storage, chlorine cylinders etc. |  |  |  |  | hence total Area = |  |  | 172.666 |  | ²
| Hence Provide room Dimension : |  |  |  |  | Length = | 15 |  | Width = | 12
|  |  | Room Area |  | = | ( 15 x 12 ) = |  | 180 |  | ²
| Area required is |  | ( < ) Greater than |  |  | Room Area provided, hence |  |  |  | Ok.
Chemical Dissolving Tanks :
| Total quantity of Alum, Lime & Soda |  |  |  | = | ( 119984.4 + 221345.89 + 156698.69 )
[5 empty] | = | 498028.98
Total quantity of Alum, Lime & Soda / Day |  |  |  |  | = | 498028.98 |  | = | 2766.83
180
| Number of Bags required |  |  |  | = | 2766.83 |  | = | 55.3 | 56
50
| 15 |  | each heep |  | = | ( 56 / 15 ) = |  | 3.7333 |  | no. of heeps
| 0.2 |  |  | ² , then total area required = |  |  |  | 0.75 |  | ²
| Hence Provide room Dimension : |  |  |  |  | Length = | 1.5 |  | Width = | 1.5
|  |  | Room Area |  | = | ( 1.5 x 1.5 ) = |  | 2.25 |  | ²
| Area required is |  | ( < ) Greater than |  |  | Area provided, hence |  |  | Ok.
Chemical Solution Tanks :
Total quantity of Alum, Lime & Soda / Day |  |  |  |  | = | 2766.83 | [6 empty] | alum | 1.76
[13 empty] | lime | 3.35
| Hence Solution required per day |  |  |  | = | 2766.83 | 20 | = | 55336.6 | Liter / Day |  |  | soda | 1.1
| Hence Solution required per day |  |  |  | = | 55336.6 |  | = | 38.43 | Liter / Min |  |  |  | 2.07
[6 empty] | 24 | 60
Quantity of solution for |  |  | 8 |  | = | 38.43 | 60 | 8 | 18446.4
[5 empty] | = | 18446.4 | 18.4464 |  | ³
1000
| Assuming Depth of Tank = |  |  | 1.2 | & Free Board |  |  | 0.3
| Dimension of Solution Tank |  |  |  | = | 4.5 | 3.5 |  | 1.5
| Volume of Solution Tank |  |  |  | = | 23.625 | ³
Summary
| S.No. | Particulars |  |  |  |  | Values
| 1 | Per Day Alum Required |  |  |  |  | 666.58
| 2 | Hydrated Lime Required |  |  |  |  | 92.24
| 3 | Soda required |  |  |  |  | 65.3
| 4 | Size of Chemical Dissolving tanks |  |  |  |  | 1.5 |  | 1.5
| 5 | Size of Chemical Solution tanks |  |  |  |  | 4.5 x 3.5 x 1.5

## Rapid mix unit
Design Criteria for Mechanical Rapid Mix Unit
| Detention Time |  |  | = | 30 | 60
| Velocity of Flow |  |  | = | 4 | 9
| Depth |  |  | = | 1 | 3
| Power Required |  |  | = | 0.041 |  | 1000 | 3 / Day
| Impeller Speed |  |  | = | 100 | 250
| Loss of Head |  |  | = | 0.4 | 1
Mixing device be capable of creating a velocity gradiend
|  |  |  | = | 300 | / sec / m depth
Ratio of impeller diameter to tank diameter = | [5 empty] | 0.2 | 0.4
Ratio of Tank Height to diameter |  |  |  | = | 1 | 3
Design Calculations
| Design Flow |  |  | = | 0.1543 | ( 24 x 60 x 60 )
|  |  |  | = | 13331.52 | m 3 / Day
| Detention Time |  |  | = | 30
Ratio of Tank Height to diameter |  |  |  | = | 1.5
Ratio of impeller dia. to tank dia. = |  |  |  |  | 0.3
| Impeller Speed |  |  | = | 120
| Assume Temperature |  |  | = | 20 | 0 C
i) | Dimension of Tank :
| Volume |  |  | = | 4.629 | ³
| Diameter D |  |  | = | 1.6
| Height of Tank |  |  | = | 4.629 | 1 | 2.3
[5 empty] | ( Π / 4 ) | 1.6 x 1.6
|  |  |  | = | 2.37 | (Say)
| Tank free board |  |  | = | 0.23
| Total Height of Tank |  |  | = | ( 2.37 + 0.23 ) = |  | 2.6
ii) | Power Requirement :
| Power Spend |  |  | = | 5.47
iii) | Dimensions of Flat Blade & Impeller :
| Diameter of Impeller |  |  | = | 0.65
Velocity of Tip Impeller ( V T ) |  |  |  | = | 4.08
| Area of Blade |  |  | = | A B
Power Spent
| Let C D = | 1.8 |  | and V R = |  | ( 3/4 ) x V T
» | 5.47 | 1000 | 1.8 |  | 1000 | A B x ( | 3/4 ) x | 4.08
2
» | A B = | 1.99 | ²
| Hence Provide |  | 8 | Blades of |  | 0.5 | 0.5
| Area of Blade Provided = |  |  |  | ( 0.5 x 0.5 ) x 8 = |  | 2 | ²
| Provide | 4 |  | 1.5 |  |  | projecting | 0.2
Provide Inlet & Outlet Pipes of |  |  |  |  | 250 | diameter.
iv) | Summary
| S.No. | Particulars |  |  |  |  | Values
| 1 | Detention Time |  |  |  |  | 30
| 2 | Speed of impeller |  |  |  |  | 120
| 3 | Height of Tank |  | 0.23 |  |  | 2.6
| 4 | Power Required |  |  |  |  | 5.47
| 5 | Number of Blade |  |  | 0.5 | 0.5 | 8
| 6 | Number of Baffles |  |  | 1.5 |  | 4
| 7 | Diameter of Inlet & Outlet Pipes |  |  |  |  | 250

## Clariflocculator
Design Of Clariflocculator
Clariflocculator
The coagulation & sedimentation processes are effectively incorporated in a single unit in the Clariflocculator. Sometimes clarifier & Clariflocculator are designed as separate units.
All these units consists of 2 or 4 flocculating paddles placed equidistantly. These paddles rotate on their vertical axis. The flocculating paddles may be of rotor-stator type. Rotating in opposite direction above the vertical axis. The clarification unit outside the flocculation compartment is served by inwardly raking rotating blades. The water mixed with chemical is fed in the flocculator compartment fitted with paddles rotating at low speeds thus forming flocs.
The flocculated water passes out from the bottom of the flocculation tank to the clarifying zone through a wide opening. The area of the opening being large enough to maintain a very low velocity. Under quiescent conditions, in the annular setting zone the floc embedding the suspended particles settle to the bottom & the clear effluent overflows into the peripheral launder.
Design Criteria : ( Flocculator )
Depth of Tank |  |  |  | = | 3 | 4.5
Detention Time |  |  |  | = | 30 | 60
Velocity of Flow |  |  |  | = | 0.2 | 0.8
Total Area of Paddles |  |  |  | = | 10 | 25
Range of peripheral velocities of blades |  |  |  | = | 0.2 | 0.6
Velocity Gradient ( G ) |  |  |  | = | 10 | 75
Dimension Less Factor G t |  |  |  | = | 10 | 4 to 10 | 5
Power Consumption |  |  |  | = | 10 | 36
Outlet Velocity |  |  |  | = | 0.15 | 0.25
Design Criteria : ( Clarifier )
Assuming a Surface Overflow rate |  |  |  | = | 40 | 3 / m 2 / Day
Depth of Water |  |  |  | = | 3 | 4.5
Weir Loading |  |  |  | = | 300 | 3 / m 2 / Day | [5 empty] | 3.75
Storage of Sludge |  |  |  | = | 25
Floor Slope |  |  |  | = | 12
|  |  |  | = | 8.3333 | for mechanically cleaned tank
Slope for Sludge Hopper |  |  |  | = | 1.2 | ( V : H )
Scraper Velocity |  |  |  | = | 1 | 45 | 80
Velocity of water at outlet chamber |  |  |  | = | 40
42.5
Assumption
Average Outflow from clariflocculator |  |  |  | = | 555.48 | 3 / hour
Water Lost in desludging |  |  |  | = | 2
Design Average Period |  |  |  | = | 555.48 | 2 | 555.48 |  |  |  | 11.1096
|  |  |  | = | 555.48 | 11.11 |  |  |  |  | 566.5896
|  |  |  | = | 566.59 | 3 / hour
Detention Period |  |  |  | = | 30
Average Value of Velocity Gradient |  |  |  | = | 30 | sec - 1
0.15739
Design Of Influent Pipe | [9 empty] | 0.20049
|  | Discharge ( Q ) |  | = | 0.1543 | 3 / sec.
| Assuming Velocity ( V ) |  |  | = | 1 |  |  |  |  | 0.44776
»
Hence Diameter ( d ) = |  |  | 0.1543 | 4 | 1/2 | 0.44335
|  |  | 1 | Π
Provide an influent pipes of |  |  | 450 | diameter.
Design Of Flocculatior : Wall
Volume of flocculator |  |  |  | = | 566.59 | 30 | 283.3 | ³
60
Provide a Water Depth |  |  |  | = | 3.5
Plan Area of flocculator |  |  |  | = | 283.3 | 80.94 | ²
3.5
Diameter of Flocculator ( D ) | [9 empty] | 10.1542
|  |  |  | = | 80.94 | 1/2 | 10.15 | 10.2
Π
Diameter of Inlet Pipes ( D P ) |  |  |  | = | 0.45
Provide a Tank Diameter of |  |  | 10.2
Dimension Of Paddles :
Here :
|  |  | P | = | Power dissipated in watts i.e. |  |  | N.m / s
|  |  | μ | = | Absolute or Dynamic Viscosity of Raw Water in N.s / m 2
|  |  | G | = | Temporal Mean Velocity Gradient in ( sec -1 )
|  |  | V | = | Volume of raw water to which P is applied in m 3
|  |  |  | = | ( Π / 4 ) x | ( 10.2 x 10.2 ) x 3.5 = |  | 285.85 | ³
= | 30 x 30 x | 0.89 | 285.85 | = | 228.97
1000
Power Input =
| C d = | 1.8
| ρ = | 995 | 3 ( 25 0 C )
| v = | Velocity of tip of blade = |  |  | 0.4
| ν = | Velocity of water tip of blade = ( 0.25 x |  |  |  | 0.4 | 0.1
» | 228.97 | = ( 1 / 2 ) x 1.8 x 995 x ( 0.4 - 0.1 ) |  |  |  | 3 x A P
|  |  | » A P | = | 9.47 | ²
Ratio of Paddles to C / S of Flocculator
| 9.47 | ( A P ) x ( | 10.2 - 0.75 ) x 3.5 x 100 = |  |  | 9.11 | 10 | 25
|  |  | Provide A P = |  | 10.5117 | ²
|  | A P = | 10.5117 | Π | x ( 10.2 - 0.75 ) x 3.5 x 100 = |  |  | 10.12
|  | ( Which is | Acceptable, hence O.K. )
Provide | 5 | of paddles | 3.5 |  | 0.7
1 | ( One ) | Shaft will support |  | 5 | Paddles.
The Paddles will rotate at an rpm of |  |  |  | 4
| V = 2 x Π x r x N |  | = 2 x 3.14 x r x ( 4 / 60 ) = 0.4
60
|  |  | » r = |  | 0.955 | 1
r = | Distance of Paddle from C 1 of vertical shaft.
Let velocity of water below the partition wall between the flocculator & clarifier be | [7 empty] | 0.3
| Area = | 555.48 | 0.3 |  | 0.514 | ²
| Depth below partition Wall = |  |  |  | 0.514 | ( Π x | 10.2
|  |  |  | = | 0.016
25 |  |  |  |  | 0.25 | 3.5 | 0.875 |  |  | 0.875
| Provide Slope for Bottom = |  |  |  | 8.3333 |  |  |  |  | 4.691
Total Depth of Tank at Partition Wall = |  |  |  |  | 0.29167 | 0.3 | 3.5 + 0.016 + 0.875 ) | [5 empty] | 0.28
|  |  |  | = | 4.691 | 4.7
Design Of Clarifier
Assuming a Surface Overflow rate |  |  |  | = | 40 | 3 / m 2 / Day
Surface Of Clariflocculator |  |  |  | = | 555.48 | 24 | 333.288 | ²
40
D cf = | Diametre of Clariflocculator
Π x ( D cf 2 - |  | 10.2 | 10.2 | = | 333.288
4
|  |  | D cf | = | 1333.152 | 104.04 | 1/2 |  |  |  | 1333.16 | 104.04
Π
|  |  |  | = | 22.992 | 23 |  |  |  |  | 37.9104 |  | 528.5401
| Length of Weir |  |  | = | Π x D cf | 23 |  | 72.22
| Weir Loading |  |  | = | 555.48 | 24 | 184.6 | 3 / Day / m |  |  | 3.1405 |  | 424.5001
72.22
According to manual of govt. of india, if it is well clarifier, then it can be exceed upto | [7 empty] | 1500
Summary
S.No. | Particulars |  |  |  |  | Values
1 | Detention Period |  |  |  |  | 30
2 | Diameter Of Influent Pipes |  |  |  |  | 0.45
3 | Overall Depth of Flocculator |  |  |  |  | 3.5
4 | Diameter of Tank |  |  |  |  | 10.2
5 | No. of Paddles |  |  |  |  | 5
6 | Distance of Shaft from C.L. of Flocculator
7 | Paddles Rotation (RPM) |  |  |  |  | 4
8 | Distance of Paddle from C.L. of vertical Shaft |  |  |  |  | 1
9 | Slope of Bottom ( % ) |  |  |  |  | 8.3333
10 | Total Depth of Partition Wall |  |  |  |  | 4.7
11 | Diameter of Clariflocculator |  |  |  |  | 23

## Rapid gravity Filter
Design Of Rapid Gravity Filter
a) | Design Criteria : ( Rapid Sand Filter )
| Rate Of Filteration |  |  |  | = | 5 | 7 | 3 / m 2 / Day
| Maximum surface area of One Bed |  |  |  | =
Minimum Overall Depth Of Filter Unit Including a Free Board of | [6 empty] | 0.5
[5 empty] | = | 2.6
| Effective size Of Sand |  |  |  | = | 0.45 | 0.7
| Uniformity Co-efficient For Sand |  |  |  | = | 1.3 | 1.7
Ignition Loss Should Not Exceed |  |  |  | 0.7 |  | percent by weight
| Specific Gravity |  |  |  | = | 2.55 | 2.65 | [5 empty] | 1.5
Wearing Loss is not greater than |  |  |  | 3
| Minimum Number Of Units |  |  |  | = | 2
| Depth Of Sand |  |  |  | = | 0.6 | 0.75
| Standing Depth of water over the filter |  |  |  | = | 1 | 2
| Free Board is less than |  |  | 0.5
b) | Problem Statement :
| Net Filtered Water |  |  |  | = | 555.48 | 3 / hour
| Quantity of Backwash water used |  |  |  | = | 2
| Time Lost During Backwash |  |  |  | = | 30
| Design Rate Of Filteration |  |  |  | = | 5 | 3 / m 2 / Day
| Length & Width Ratio |  |  |  | = | 1.25 | 1.33
| Under Drainage System |  |  |  | = | Central Manifold With Laterals
| Size of Perforations |  |  |  | = | 13
c) | Design Calculations
| Water Flow Required |  |  |  | = | 555.48 | 3 / hour
| Design Flow for Filter |  |  |  | = | 555.48 x ( 1 + 0.02 ) x |  |  | 24
23.5
[5 empty] | = | 578.64 | 3 / hour
| Plan Area For Filter |  |  |  | = | 578.64 | 115.728 | ² ≡ | 116 | ²
5
| Using | 2 | Units
| Hence Plan Area of One Unit |  |  |  | = | 116 | 58 | ²
2
| Length x | Width = | L x | 1.25 | = | 58 | ²
|  |  | » | Length L | = | 58 | 1/2
1.25
[5 empty] | = | 6.8
|  |  |  | Width | = | 1.25 | 6.8 | 8.5 | 8.6
| Provide | 2 | Units, each with a dimension of = |  |  |  | 8.6 | 6.8
Estimation Of Sand Depth :
It is checked against break through of floc.
Using Hudson Formula -
|  |  |  | Q x d 3 x h | = | 293223
|  |  |  | ℓ |  | L
|  | Where | Q, d, h & ℓ are in |  | m | 3 / m 2 / hr, mm, m and m respectively
| Assume | B = | 4 | ( Poor Response ) < Average degree of pre-treatment
10000
|  | h = | 2.5 | ( Terminal Head Loss )
|  | Q = | 5 | 3 / m 2 / hr | ( Assuming 100 % overload of filter )
|  | d = | 0.6 | ( Mean Diameter )
| » | 10 | 0.6 x 0.6 x 0.6 x 2.5 |  | = | 4 | 293223
|  |  | ℓ |  |  | 10000
|  |  |  | ℓ | = | 46.04 | { or ( > ) greater than }
| Hence provide depth of sand bed = |  |  |  |  | 60
Estimation Of Gravel & Size Gradation :
| Assuming size gradation of |  |  | 2 |  | 40 | at bottom using empirical
|  | formula : | 2.54 | R x ( log d )
|  | Where : |  | R | = | 12 | 10 | 14 | )
| The Units of L & d are |  |  | cm & mm, respectively.
Size |  | 2 | 5 | 10 | 20 |  | 40
Depth (cm ) |  | 9.2 | 21.3 | 30.5 | 40 |  | 49 |  |  |  | 29.3763
Increment |  | 9.2 | 12.1 | 9.2 | 9.5 |  | 9
| Hence provide |  | 50 | depth of gravel.
Estimation Of Under Drainage System :
| Plan Area of each filter |  |  |  | = | 8.6 | 6.8
[5 empty] | = | 58.48 | ²
| Total Area of perforation |  |  |  | = | 3 | 58.48 | 0.17544 |  | ²
1000
[8 empty] | 1754.4 |  | ²
| Total Cross Section Area of Laterals |  |  |  | = | 3 | Area of perforation )
[5 empty] | = | 3 | 1754.4 | 5263.2 |  | ²
| Area of Central Manifold |  |  |  | = | 2 | Area of Laterals )
[5 empty] | = | 2 | 5263.2 | 10526.4 |  | ²
| Diameter of Central Manifold |  |  |  | = | 10526.4 | 4 | 115.7991
Π
| Providing a commercially available diameter of |  |  |  | 100
| Assuming spacing for laterals |  |  |  | = | 20
| Number of Laterals |  |  |  | = | 8.6 | 100 | 43
20
|  |  |  | D | = | 61.2 | 4 | 8.8296 | 90 |  |  | 8.8296
Π
| Number of perforations / laterals = |  |  |  |  | 86
Length of One lateral = ( 1 ) width of filter - ( 1 ) diameter of manifold
|  |  |  | 2 |  | 2
|  |  | = ( 1 x | 6.8 | 1 | 1 | 2.9
|  |  | 2 |  | 2
| Let n be the total number of perforation of |  |  |  | 13 | [6 empty] | 1322.4287
|  | Total Area of perforation |  |  | » | n x Π | 1.3 | ² = | 1754.4
4
|  |  |  | » n | = | 1322.43 | 1322
|  | Number of Perforation or Laterals |  |  | = | 1322 | 15.3721 | 16
86
|  |  | Spacing of Perforation |  | = | 2.9 | 100 | 18.125
16
180
|  | 16 | 13 |  |  |  | 180
Computation Of Wash Water Troughs :
|  | Wash Water Rate |  |  | = | 36 | 3 / m 2 / hour
| Wash Water discharge for one filter |  |  |  | = | 36 | 58.48 | 2105.28 | 3 / hour
[5 empty] | = | 0.5848 | 3 / sec.
| Assuming a spacing of |  | 1.8 | wash water trough which will run parallel to the longer
dimension of the filter unit.
|  |  | Number of trough |  | = | 6.8 | 3.78 | 4
1.8
|  | Discharge per unit trough |  |  | = | 0.5848 | 0.1462 | 3 / sec.
4
| For a width of |  | 0.4 | the water depth at upper end is given by :
|  |  |  | 0.1462 | = | 1.376 | 0.4 | 3/2
|  |  |  | h | = | 0.1462 | 2/3 | 0.41 | 0.5
[6 empty] | 1.376 | 0.4
|  |  |  | Freeboard | = | 0.1
| Provide | 4 | troughs of | 0.49 | Wide & |  | 0.5 | deep in each filter.
Total Depth Of Filter Box :
Depth of filter box = ( depth of under drain + gravel + sand + water depth + free board )
|  |  | = | 900 | 500 + 600 + |  | 2200 | 300
|  |  | = | 4500
Design Of Filter Air Wash :
| Assume Rate at which air is supplied |  |  |  | = | 1.5 | 3 / m 2 / min.
|  | Duration of Air Wash |  |  | = | 3
| Total Quantity of air per unit bed |  |  |  | = | 1.5 | 3 | 8.6 | 6.8
[5 empty] | = | 263.16 | ³
Summary
| S.No. | Particulars |  |  |  |  | Values
| 1 | Number Of Units |  |  |  |  | 2
| 2 | Size Of Unit |  |  |  |  | 8.6 | 6.8
| 3 | Depth Of Sand Bed |  |  |  |  | 60
| 4 | Depth Of Gravel |  |  |  |  | 50
| 5 | Diameter Of Perforation |  |  |  |  | 13
| 6 | Diameter Of Central Manifold |  |  |  |  | 100
| 7 | Spacing For Laterals |  |  |  |  | 20
| 8 | Number Of Laterals |  |  |  |  | 86
| 9 | Diameter Of Laterals |  |  |  |  | 90
| 10 | Number Of Perforations |  |  |  |  | 16
| 11 | Number Of Trough |  |  |  |  | 4
| 12 | Size Of Trough |  |  |  |  | 0.4 | 0.49
| 13 | Total Depth Of Filter Box |  |  |  |  | 4500
| 14 | Duration of Air Wash |  |  |  |  | 3
| 15 | Total Quantity Of Air Required Per Unit Bed | [5 empty] | 263.16 | ³

## Disinfection Unit
Design Of Disinfection Unit
a) | Chlorination
Disinfection should not only remove the existing bacteria from water but also ensure their immediate killing even afterwards, in the distribution system.
b) | Design Criteria ( Chlorination )
| → Chlorine Dose |  |  | = | 1.4 | ( Rainy Season )
|  |  |  | = | 1 | ( Winter Season )
|  |  |  | = | 0.6 | ( Summer Season )
| → Residual Chlorine |  |  | = | 0.1 | 0.2 | ( Minimum )
| → Contact Period |  |  | = | 20 | 30
c) | Design Calculations
| Rate of Chlorine required, to disinfect water be = |  |  |  |  | 2
|  | Chlorine required Per Day |  | = | 13.33 | 1000000 | 1.4 | 1
1000000
|  |  |  | = | 18.662
|  | 6 |  | = | 18.662 | 180 | 3359.16
| Number of Cylinder |  | ( One Cylinder contain |  | 16 | 3359.16 | 2 | 419.895
16
| Number Of Cylinders used per day |  |  | = | 2 | 16
d) | Summary
| S.No. | Particulars |  |  |  | Values
| 1 | Chlorine required per day |  |  |  | 18.662
| 2 | Number Of Cylinders required per day |  |  |  | 2 | 16